## Calculation
Heat Loss From An Insulated Pipe
CheGuide.com | [6 empty] | Date | 9-July-16
Chemical Engineer's Guide | [6 empty] | By | CheGuide
Pipe | Inside Diameter (D1) |  | 77.9272 | mm
| Outside Diameter (D2) |  | 88.9 | mm
Operating Temperature |  |  | 180 | °C
Ambient Temperature |  |  | 28 | °C
Wind Speed |  |  | 3.5 | m/s
Insulation |  |  |  |  | Insulated Pipe
Type |  |  | Calcium Silicate |  | Surface Temperature |  |  | 33.4285 | °C
Surface Emmisivity |  |  | 0.9 |  | Heat Loss |  |  | 73.12 | W/m
Thickness |  |  | 50 | mm | Bare Pipe
Outside Diameter |  | D3 | 188.9 | mm | Surface Temperature |  |  | 179.486 | °C
[5 empty] | Heat Loss |  |  | 1374.0012 | W/m
Calculation for Insulated Pipe
|  |  | Iterations |  | 1 | 2 | 3 | 4 | 5
Surface Temperature |  |  | t_surface | °C | 29 | 33.4325 | 33.4285 | 33.4285 | 33.4285
Interface Temperature |  |  | t_interface | °C | 179 | 179.9727 | 179.9726 | 179.9726 | 179.9726
Air Properties
Average Film Temperature |  |  | t_average | °C | 28.5 | 30.7162 | 30.7143 | 30.7143 | 30.7143
|  |  |  | °K | 301.65 | 303.8662 | 303.8643 | 303.8643 | 303.8643
Thermal Conductivity |  |  | k | W/m.K | 0.026387 | 0.026562 | 0.026562 | 0.026562 | 0.026562
Viscosity |  |  | µ | N/s.m² | 1.856e-05 | 1.8667e-05 | 1.8667e-05 | 1.8667e-05 | 1.8667e-05
Prandtl Number |  |  | Pr |  | 0.7069 | 0.70638 | 0.70638 | 0.70638 | 0.70638
Expansion Coefficient |  |  | β | 1/K | 0.0033151 | 0.0032909 | 0.0032909 | 0.0032909 | 0.0032909
Air Density |  |  | ρ | Kg/m³ | 1.1716 | 1.163 | 1.1631 | 1.1631 | 1.1631
Kinematic Viscosity |  |  | ν | m2/s | 1.6063e-05 | 1.6273e-05 | 1.6273e-05 | 1.6273e-05 | 1.6273e-05
Specific Heat |  |  | Cp | kJ/Kg.K | 1.005 | 1.0051 | 1.0051 | 1.0051 | 1.0051
alpha |  |  | α | m²/s | 2.2717e-05 | 2.3038e-05 | 2.3038e-05 | 2.3038e-05 | 2.3038e-05
Reynold's Number |  |  | Re |  | 41160.5106 | 40628.9799 | 40629.4477 | 40629.4469 | 40629.447
Rayleigh Number |  |  | Ra |  | 600738.3959 | 3153305.5093 | 3151113.1515 | 3151116.7379 | 3151116.7319
Air Film Resistance
Radiation |  |  | h_radiation | W/m².K | 5.6031 | 5.7279 | 5.7278 | 5.7278 | 5.7278
Convection
Forced Convection |  |  | Nu_forced |  | 121.6604 | 120.658 | 120.6588 | 120.6588 | 120.6588
|  |  | h_forced | W/m².K | 16.9944 | 16.9661 | 16.9661 | 16.9661 | 16.9661
Free Convection |  |  | Nu_free |  | 12.6037 | 20.1509 | 20.1468 | 20.1468 | 20.1468
|  |  | h_free | W/m².K | 1.7606 | 2.8335 | 2.8329 | 2.8329 | 2.8329
Combined Convection |  |  | Nu_Combined |  | 121.6639 | 120.6814 | 120.6823 | 120.6823 | 120.6823
|  |  | h_convection | W/m².K | 16.9949 | 16.9694 | 16.9694 | 16.9694 | 16.9694
Overall air side HTC |  |  | h_air | W/m².K | 22.5979 | 22.6973 | 22.6972 | 22.6972 | 22.6972
Pipe Resistance
Pipe Thermal conductivity |  |  | k_pipe | W/m.K | 56.0454 | 56.0454 | 56.0454 | 56.0454 | 56.0454
Pipe wall resistance |  |  | r_pipe | m².K/W | 0.00022201 | 0.00022201 | 0.00022201 | 0.00022201 | 0.00022201
Insulation Resistance
Average Insulation temperature |  |  |  | °K | 377.15 | 379.8526 | 379.8506 | 379.8506 | 379.8506
Insulation Thermal conductivity |  |  | k_insulation | W/m.K | 0.059636 | 0.059854 | 0.059854 | 0.059854 | 0.059854
Insulation resistance |  |  | r_insulation | m².K/W | 1.1937 | 1.1894 | 1.1894 | 1.1894 | 1.1894
Overall Resistance |  |  | r_overall | m².K/W | 1.2382 | 1.2336 | 1.2336 | 1.2336 | 1.2336
Heat Flow |  |  | Q | W/m² | 122.7624 | 123.2127 | 123.2124 | 123.2124 | 123.2124
Interface Temperature |  |  | T_interface | °C | 179.9727 | 179.9726 | 179.9726 | 179.9726 | 179.9726
Surface Temeperature |  |  | T_surface | °C | 33.4325 | 33.4285 | 33.4285 | 33.4285 | 33.4285
Heat Loss per Unit Length |  |  |  | W/m | 72.8529 | 73.1202 | 73.12 | 73.12 | 73.12
Calculation for Bare Pipe
|  |  | Iterations |  | 1 | 2 | 3 | 4 | 5
Surface Temperature |  |  | t_surface | °C | 29 | 179.5558 | 179.4859 | 179.486 | 179.486
Bare Pipe Emissivity |  |  |  |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Air Properties
Average Film Temperature |  |  | t_average | °C | 28.5 | 103.7779 | 103.743 | 103.743 | 103.743
|  |  |  | °K | 301.65 | 376.9279 | 376.893 | 376.893 | 376.893
Thermal Conductivity |  |  | k | W/m.K | 0.026387 | 0.032148 | 0.032145 | 0.032145 | 0.032145
Viscosity |  |  | µ | N/s.m² | 1.856e-05 | 2.2011e-05 | 2.201e-05 | 2.201e-05 | 2.201e-05
Prandtl Number |  |  | Pr |  | 0.7069 | 0.69258 | 0.69259 | 0.69259 | 0.69259
Expansion Coefficient |  |  | β | 1/K | 0.0033151 | 0.002653 | 0.0026533 | 0.0026533 | 0.0026533
Air Density |  |  | ρ | Kg/m3 | 1.1716 | 0.93761 | 0.9377 | 0.9377 | 0.9377
Kinematic Viscosity |  |  | ν | m²/s | 1.6063e-05 | 2.3781e-05 | 2.3777e-05 | 2.3777e-05 | 2.3777e-05
Specific Heat |  |  | Cp | kJ/Kg.K | 1.005 | 1.0108 | 1.0108 | 1.0108 | 1.0108
alpha |  |  | α | m²/s | 2.2717e-05 | 3.4499e-05 | 3.4493e-05 | 3.4493e-05 | 3.4493e-05
Reynold's Number |  |  | Re |  | 19370.9338 | 13084.1099 | 13086.2284 | 13086.2271 | 13086.2271
Rayleigh Number |  |  | Ra |  | 62617.3667 | 3378022.0833 | 3377897.1781 | 3377897.2581 | 3377897.258
Air Film Resistance
Radiation |  |  | h_radiation | W/m².K | 4.9805 | 10.1098 | 10.1067 | 10.1067 | 10.1067
Convection
Forced Convection |  |  | Nu_forced |  | 77.7239 | 61.6709 | 61.6767 | 61.6767 | 61.6767
|  |  | h_forced | W/m².K | 23.0696 | 22.3013 | 22.3016 | 22.3016 | 22.3016
Free Convection |  |  | Nu_free |  | 6.8847 | 20.5009 | 20.5007 | 20.5007 | 20.5007
|  |  | h_free | W/m².K | 2.0435 | 7.4135 | 7.4128 | 7.4128 | 7.4128
Combined Convection |  |  | Nu_Combined |  | 77.7251 | 61.8583 | 61.8641 | 61.8641 | 61.8641
|  |  | h_convection | W/m².K | 23.07 | 22.369 | 22.3693 | 22.3693 | 22.3693
Overall air side HTC |  |  | h_air | W/m².K | 28.0505 | 32.4789 | 32.476 | 32.476 | 32.476
Pipe Resistance
Pipe Thermal conductivity |  |  | k_pipe | W/m.K | 56.0454 | 56.0454 | 56.0454 | 56.0454 | 56.0454
Pipe wall resistance |  |  | r_pipe | m².K/W | 0.00010448 | 0.00010448 | 0.00010448 | 0.00010448 | 0.00010448
Overall Resistance |  |  | r_overall | m².K/W | 0.035754 | 0.030894 | 0.030896 | 0.030896 | 0.030896
Heat Flow |  |  | Q | W/m² | 4251.2142 | 4920.0913 | 4919.6641 | 4919.6644 | 4919.6644
Interface Temperature |  |  | T_interface | °C | 179.5558 | 179.4859 | 179.486 | 179.486 | 179.486
Heat Loss per Unit Length |  |  |  | W/m | 1187.3114 | 1374.1204 | 1374.0011 | 1374.0012 | 1374.0012
D1
D2
D3
Air
Insulation
Pipe
Fluid

## Air_Properties
4th Order Polynomial Fitting
Thermophysical properties of Air | [12 empty] | Specific Heat Curve Fitting
CheGuide.com | [9 empty] | Date | 19-Dec-15 |  | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
Chemical Engineer's Guide | [9 empty] | By | CheGuide |  | 3.0372e-13 | -1.1132e-09 | 1.4438e-06 | -0.00056534 | 1.0722
[13 empty] | 1.0101e-13 | 2.2348e-10 | 1.6871e-07 | 4.9894e-05 | 0.0046704
| Literature Values | [5 empty] | Calculated Values | [5 empty] | 0.99904 | 0.0016371 | #N/A | #N/A | #N/A
T | Cp | µ.10^7 | ν.10^6 | k.10^3 | α.10^6 | Pr | Cp | µ.10^7 | ν.10^6 | k.10^3 | α.10^6 | Pr
K | kJ/Kg.K | N.s/m2 | m2/s | w/m.K | m2/s |  | kJ/Kg.K | N.s/m2 | m2/s | w/m.K | m2/s |  | Viscosity Curve Fitting
100 | 1.032 | 71.1 | 2 | 9.34 | 2.54 | 0.786 | 1.0291 | 71.1802 | 1.9484 | 9.3969 | 2.7587 | 0.78429 | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
150 | 1.012 | 103.4 | 4.426 | 13.8 | 5.84 | 0.758 | 1.0163 | 103.1638 | 4.4503 | 13.7703 | 5.6942 | 0.75944 | -1.5858e-10 | 5.115e-07 | -0.00072457 | 0.79781 | -1.8504
200 | 1.007 | 132.5 | 7.59 | 18.1 | 10.3 | 0.737 | 1.0085 | 132.5665 | 7.6438 | 18.0556 | 10.0989 | 0.73841 | 1.0542e-11 | 2.3323e-08 | 1.7606e-05 | 0.005207 | 0.4874
250 | 1.006 | 159.6 | 11.44 | 22.3 | 15.9 | 0.72 | 1.0049 | 159.6885 | 11.4784 | 22.2253 | 15.7586 | 0.72108 | 1 | 0.17085 | #N/A | #N/A | #N/A
300 | 1.007 | 184.6 | 15.89 | 26.3 | 22.5 | 0.707 | 1.005 | 184.8065 | 15.907 | 26.2564 | 22.4795 | 0.7073
350 | 1.009 | 208.2 | 20.92 | 30 | 29.9 | 0.7 | 1.0081 | 208.1733 | 20.8857 | 30.1309 | 30.0878 | 0.69688 | Kinematic Viscosity Curve Fitting
400 | 1.014 | 230.1 | 26.41 | 33.8 | 38.3 | 0.69 | 1.0136 | 230.0178 | 26.3743 | 33.8354 | 38.4304 | 0.6896 | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
450 | 1.021 | 250.7 | 32.39 | 37.3 | 47.2 | 0.686 | 1.0212 | 250.5454 | 32.3357 | 37.3613 | 47.3743 | 0.68521 | 2.2585e-11 | -8.3209e-08 | 0.00017267 | 0.010637 | -0.76108
500 | 1.03 | 270.1 | 38.79 | 40.7 | 56.7 | 0.684 | 1.0304 | 269.9375 | 38.7363 | 40.7048 | 56.8069 | 0.68345 | 3.4323e-12 | 7.5936e-09 | 5.7324e-06 | 0.0016953 | 0.15869
550 | 1.04 | 288.4 | 45.57 | 43.9 | 66.7 | 0.683 | 1.0406 | 288.3516 | 45.5458 | 43.8669 | 66.636 | 0.68399 | 1 | 0.055627 | #N/A | #N/A | #N/A
600 | 1.051 | 305.8 | 52.69 | 46.9 | 76.9 | 0.685 | 1.0517 | 305.9217 | 52.7375 | 46.8532 | 76.7896 | 0.6865
650 | 1.063 | 322.5 | 60.21 | 49.7 | 87.3 | 0.69 | 1.0633 | 322.7578 | 60.2878 | 49.6741 | 87.2162 | 0.6906 | Thermal Conductivity Curve Fitting
700 | 1.075 | 338.8 | 68.1 | 52.4 | 98 | 0.695 | 1.0751 | 338.9462 | 68.1768 | 52.3449 | 97.8845 | 0.69589 | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
750 | 1.087 | 354.6 | 76.37 | 54.9 | 109 | 0.702 | 1.0869 | 354.5495 | 76.3877 | 54.8856 | 108.7836 | 0.70194 | 3.1718e-11 | -5.9023e-08 | 4.5853e-06 | 0.088868 | 0.52007
800 | 1.099 | 369.8 | 84.93 | 57.3 | 120 | 0.709 | 1.0985 | 369.6063 | 84.9073 | 57.3208 | 119.9229 | 0.70827 | 3.7221e-12 | 8.2349e-09 | 6.2164e-06 | 0.0018385 | 0.17209
850 | 1.11 | 384.3 | 93.8 | 59.6 | 131 | 0.716 | 1.1098 | 384.1316 | 93.7257 | 59.68 | 131.3322 | 0.7144 | 0.99999 | 0.060325 | #N/A | #N/A | #N/A
900 | 1.121 | 398.1 | 102.9 | 62 | 143 | 0.72 | 1.1207 | 398.1165 | 102.8363 | 61.9975 | 143.0615 | 0.71979
950 | 1.131 | 411.3 | 112.2 | 64.3 | 155 | 0.723 | 1.1312 | 411.5284 | 112.2361 | 64.3122 | 155.1814 | 0.72388 | Alpha Curve Fitting
1000 | 1.141 | 424.4 | 121.9 | 66.7 | 168 | 0.726 | 1.1412 | 424.3108 | 121.9253 | 66.668 | 167.7825 | 0.72608 | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
[13 empty] | 1.3557e-10 | -3.8059e-07 | 0.00044648 | -0.035936 | 2.2545
Source : Fundamentals of Heat and Mass Transfer (2007), Frank P Incropera | [12 empty] | 1.1751e-11 | 2.5999e-08 | 1.9626e-05 | 0.0058045 | 0.54333
[13 empty] | 0.99999 | 0.19046 | #N/A | #N/A | #N/A
Prandtl Number Curve Fitting
[13 empty] | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
[13 empty] | -2.0844e-13 | -1.7279e-11 | 8.0062e-07 | -0.00069461 | 0.84578
[13 empty] | 8.6313e-14 | 1.9096e-10 | 1.4415e-07 | 4.2633e-05 | 0.0039907
[13 empty] | 0.99793 | 0.0013989 | #N/A | #N/A | #N/A

## Properties
Thermophysical properties of Air
CheGuide.com |  |  |  |  | Date | 19-Dec-15
Chemical Engineer's Guide |  |  |  |  | By | CheGuide
Thermal Conductivity of Plain Carbon Steel
T | K | K Calculated | 3rd Order Polynomial Curve Fitting
K | W/m.K | W/m.K | C1.T^3 | C2.T^2 | C3.T | C4
400 | 58.7 | 58.7 | 2.0833e-09 | 8.4377e-19 | -0.051083 | 79
600 | 48.8 | 48.8 | 0 | 0 | 0 | 0
800 | 39.2 | 39.2 | 1 | 0 | #N/A | #N/A
1000 | 30 | 30
Thermal Conductivity of Calcium Silicate
T | K | K Calculated
K | W/m.K | W/m.K | 4th Order Polynomial Curve Fitting
310 | 0.055 | 0.055085 | C1.T^4 | C2.T^3 | C3.T^2 | C4.T | C5
365 | 0.059 | 0.05869 | 3.1571e-13 | -7.4641e-10 | 7.3655e-07 | -0.00022488 | 0.073336
420 | 0.063 | 0.063338 | 9.115e-13 | 1.9172e-09 | 1.4674e-06 | 0.00048356 | 0.057856
530 | 0.075 | 0.074835 | 0.99986 | 0.00049963 | #N/A | #N/A | #N/A
645 | 0.089 | 0.089066
750 | 0.104 | 0.10399
Source : Fundamentals of Heat and Mass Transfer (2007), Frank P Incropera